IBM 2105 Storage Server

Maintenance Procedures

Contents

1	Introduction	3

1.1	Overview	3

1.2	Education	3

2	Safety and Inspection	4

2.1	General Information	4

2.2	Preparation	4

2.3	Branch Circuit CB Switched Off Check	5

2.4	Branch Circuit CB Switched On Check	6

2.5	Safety Labels and AC Grounds	7

2.6	Safety Labels and Grounds for the Model L1x	7

2.7	Safety Labels and Grounds for the Model D1x	8

2.8	Safety Labels and Grounds for the Model S10	8

2.9	Safety Engineering Changes	9

2.10	Safety Checks	9

2.11	Completion Report and Signature	10

2.11.1	Safety Hazards	10

3	Library Information Tables	11

3.1	General Information	11

3.2	ARTIC Port Assignments – Figure 272	12

3.3	Teach Configuration – Figure 284	13

3.4	General Library Information – Figure 285	15

3.5	Remote Support Information – Figure 286	16

3.6	LAN Information – Figure 287	17

4	Library Verification Checklist	18

4.1	General Information	18

5	Preventive Maintenance (PM)	20

5.1	General Information	20

5.2	Supplies needed	20

5.3	Procedure	20

# Introduction

## Overview

The procedures in this document ensure that a 2105 not under a TRT maintenance agreement has the necessary prerequisites installed and available to ensure a transparent transition and an uninterrupted maintenance service during the period of the TRT maintenance agreement.

## Education

All service personnel must be trained on the general maintenance agreement qualification, tailored maintenance agreement qualification, and changed machine safety inspection procedures as part of becoming a TRT Technical Service Representative (TSR). In addition, service personnel must also be trained on the 2105 prior to servicing the equipment.

# Safety and Inspection

## General Information

The safety checklist procedures in this topic ensure that a 3494 not under a TRT maintenance agreement has the necessary safety items installed and that no changes made it unsafe. Each 3494, as designed and assembled, has safety items installed to protect operators and service personnel from injury. These checklist procedures verify only these items.

The safety checklist procedures must be performed before the normal inspection for a maintenance agreement. The 3494 must be considered unsafe until the presence and condition of all checklist items are verified. If any unsafe conditions are present, you must decide how serious the hazard is and whether you can continue without first correcting the problem.

When performing the safety checklist procedures, consider the following conditions and the potential safety hazards they present:

- Electrical, especially primary power. For example, an electrically charged frame can cause serious or lethal electrical shock.

- Explosive. For example, damaged or expanding capacitors can cause serious injury.

- Mechanical hazards, such as missing safety covers, can cause injury to service personnel.

## Preparation

The following reference items are useful during the inspection:

- The LOC section of the 3494 Maintenance Information manual

- Copies of safety service memorandums (SMs) and engineering change announcements (ECAs) for this machine type

- Parts catalog

- 3494 history

- Electrical Safety for TRT Technical Service Representatives

## Branch Circuit CB Switched Off Check

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| Locate and switch off the circuit breaker (CB) for the 3494 branch circuit that supplies voltage to each receptacle |  | TRT / Customer |  |
| Perform one of the following for each receptacle: Note: There is a line cord for each control unit frame and drive unit frame in the library. If this is a metal clad connector, perform the “Safe-to-Handle Check” and the Disconnect Precautions” procedures in Electrical Safety for TRT Technical Service Representatives. (These procedures are described under “Miscellaneous Safety Tips.”) If the power cord has an insulated plug, grip the plug without touching any metal parts, and remove the plug from the customer power receptacle |  | TRT / Customer |  |
| Perform the “Power Receptacle Safety Check” in Electrical Safety for TRT Technical Service Representatives |  | TRT |  |
| DANGER Hazardous voltages are present. Do not touch the internal parts (pins and sockets) of the outlet. Measure the phase-to-ground voltage at each receptacle If a neutral is present, measure the phase-to-neutral voltage, phase-to-ground voltage, and the neutral-to-ground voltage If all voltage values are not less than 1.0 V ac, have an electrician check the circuit |  | TRT |  |

## Branch Circuit CB Switched On Check

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| Switch on the CB that supplies voltage to each receptacle for the library |  | TRT / Customer |  |
| DANGER Hazardous voltages are present. Do not touch the internal parts (pins and sockets) of the outlet. Measure the phase-to-ground voltage at each receptacle If a neutral is present, measure the phase-to-neutral voltage, phase-to-ground voltage, and the neutral-to-ground voltage Record the voltages for future reference in the checklist shown in the following table |  | TRT |  |
| Switch off the branch circuit CB before connecting the machine power cord into the outlet |  | TRT / Customer |  |

| Voltage Checklist |
| --- |
| Date | Description of circuits checked | Voltage Values | Comments | TSR |

## Safety Labels and AC Grounds

Understand the meaning of the safety labels before beginning any repair of a component with a label.

Check that the labels are located where shown in following figures. Make any necessary corrections. See IBM 3494 Tape Library Dataserver Parts Catalog for part numbers of labels in the various languages.

## Safety Labels and Grounds for the Model L1x

## Safety Labels and Grounds for the Model D1x

Use the previous figure keys 6 through 8 and 10 through 12 for the locations of the safety labels and grounds in the drive unit frame.

## Safety Labels and Grounds for the Model S10

The storage unit frame does not contain any safety labels or grounds.

## Safety Engineering Changes

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| All safety engineering changes (ECs) have been installed correctly |  | TRT |  |
| The location or list of engineering change announcements (ECAs) is accessible |  | TRT |  |

## Safety Checks

The 3494 must be powered off with the power cable disconnected.

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| All hinges and latches are in acceptable operating condition and are not broken or corroded |  | TRT |  |
| All door interlocks and safety switches are operating and are not bypassed with jumpers or taped closed |  | TRT |  |
| All ac line cords are not frayed or damaged |  | TRT |  |
| All ac line cords have the correct part number Note: See IBM 3494 Tape Library Dataserver Parts Catalog for the correct part number for the power cables. See also IBM 3494 Tape Library Dataserver Introduction and Planning Guide |  | TRT |  |
| All ground jumpers (normally green and yellow) are tightly attached. Check that all covers, housings, and metal box sides have proper ground continuity (less than 0.1 ohm) |  | TRT |  |
| All ground connections are tightly attached |  | TRT |  |
| Check from the library manager chassis to the control unit frame for proper ground continuity (less than 0.1 ohm) |  | TRT |  |
| The resistance from the library manager line cord ground pin to the frame and to the power supply covers must not be more than 0.1 ohm. For the ground connection locations, see Figure 211 on page INSP-7 |  | TRT |  |
| All safety covers (operator and service areas) are in place including those protecting mechanical devices and hot surfaces. No sharp corners or edges should be unprotected. All access covers must be in place |  | TRT |  |
| The customer’s circuit breakers and circuit panels for the 3494 frames are identified as 3494 branch circuits |  | TRT |  |
| All ac output safety covers are installed |  | TRT |  |
| No obvious non-IBM changes have been made |  | TRT |  |
| No metal filings, dirt, contaminants, water, or other fluids are present |  | TRT |  |
| There are no marks from earlier smoke or burning |  | TRT |  |
| The ac power supplies are attached tightly in place |  | TRT |  |
| The ac line cords have no frayed or damaged wiring at the PCCs |  | TRT |  |
| The resistance from the line cord ground pins and housings to all frames and to all power assembly grounds are: Line cord ground pin to frame ground resistance must not be more than 0.1 ohm Line cord housing to frame ground resistance must not be more than 0.1 ohm |  | TRT |  |
| All power wiring does not have frayed or damaged wires |  | TRT |  |
| The dc power supplies are attached tightly in place |  | TRT |  |
| All circuit breakers are the correct size. See IBM 3494 Tape Library Dataserver Parts Catalog |  | TRT |  |
| All cables, connections, and plugs do not have frayed or damaged wiring |  | TRT |  |
| All latches or clamps are in acceptable condition |  | TRT |  |

## Completion Report and Signature

- Safety inspection for machine type 3494

- General safety inspection

- Maintenance agreement qualification

After the inspection, sign and date the checklist and store it with the maintenance job paperwork.

Name										Date

### Safety Hazards

List all safety hazards, if there are none, write none.

# Library Information Tables

## General Information

The following library information tables are provided to record vital library information for new maintenance agreements or new TSRs that may not be familiar with this account.

Complete the following general information tables for this library and place the following sheets (or a copy) in the clear plastic envelope P/N 1470207 located inside the Model L1x rear door on the top of the display compartment along with any appropriate local information:

- ARTIC Port Assignments. See Figure 272 or INST-98

- Teach Configuration. See Figure 284 or INST-124

- General Library Information. See Figure 285 or INST-135

- Remote Support Information. See Figure 286 or INST-137

- LAN Information. See Figure 287 or INST-139

## ARTIC Port Assignments – Figure 272

## Teach Configuration – Figure 284

## General Library Information – Figure 285

## Remote Support Information – Figure 286

## LAN Information – Figure 287

# Library Verification Checklist

## General Information

Use the following checklist to verify that the library is installed correctly and ready for TRT maintenance.

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| All leveling pads are snug against the floor |  | TRT |  |
| The X-rail in each frame is aligned vertically and horizontally |  | TRT |  |
| The X-rail is straight and level within 3 mm over 4 frames |  | TRT |  |
| The X-rail upper and lower bearing rods on each frame are touching the previous rods |  | TRT |  |
| The rear aisle frame member of the end frames is plumb within 4 mm |  | TRT |  |
| Four frame attach brackets are installed between each expansion frame |  | TRT |  |
| All frame spacer bolts are installed between each expansion frame |  | TRT |  |
| The upper rail in each frame is locked and aligned from side-to-side |  | TRT |  |
| The center upper rail rollers do not touch the rail in any frame |  | TRT |  |
| The accessor can reach the last column of cartridges on each side without touching the X-axis bumper |  | TRT |  |
| The accessor moves freely and quietly along the length of the library |  | TRT |  |
| The lower and middle storage arrays are sitting down tight against the support bracket or drive sleeve |  | TRT |  |
| The upper storage arrays are sitting down tight against the lower storage array (or bracket) |  | TRT |  |
| There is no gap between the upper and lower storage array side brackets on either side |  | TRT |  |
| The storage array cells in each frame are not damaged or nicked and all empty cell labels are present |  | TRT |  |
| If the library has a dual gripper, storage inserts are installed and fully seated in the upper and lower two rows of each frame |  | TRT |  |
| All screw heads behind the storage array fiducials are covered with a black plastic sleeve |  | TRT |  |
| The door pin (if adjustable) touches the door support bracket on each frame when the door is closed. All doors should open and close freely |  | TRT |  |
| Each door latch is adjusted so the door is tight against the frame when the door is locked |  | TRT |  |
| If your library has an X cable with a metal band, ensure the X-axis cable tracks correctly without touching the drive covers, cable trough edge, or X-rail |  | TRT |  |
| Each 3490 CxA deck is pulled forward in the sleeve and the retaining screws are tight |  | TRT |  |
| Each 3490 CxA drive sleeve has a retaining screw installed in the rack at the rear of the sleeve |  | TRT |  |
| Each 3490 F1A drive has both slide retaining screws installed |  | TRT |  |
| Each 3590 drive has a slide retaining screw installed at the rear of the drive |  | TRT |  |
| Verify that the distance between the front of the picker reach platform and the cartridge label surface is 35 mm or less on each frame at the drive unload point and at the storage rack |  | TRT |  |
| All screw heads behind the 3490 drive fiducials are black |  | TRT |  |
| All fiducials were located successfully during the Teach operation |  | TRT |  |
| The library manager microcode and all microcode in the 3490 and/or 3590 tape subsystems is at the latest released level |  | TRT |  |
| The Verify Installation tests ran successfully on each new frame and drive |  | TRT |  |
| If the customer does not need the library immediately, run 10 cycles of the Frames Alignment test with all new frames selected and 5 cycles of the Drive Get/Put test with all new drives selected. Check the logs for errors after each test completes |  | TRT |  |
| Check the customer has sufficient cleaning cartridges that were shipped with the library |  | TRT |  |
| Ensure that the Licensed Internal Code (LIC) backup diskettes and library manager diagnostic diskettes are stored in the supplied binder SA37-0300 |  | TRT |  |
| Ensure the front and rear door keys, 3494 tools and books are close to the library for service activity |  | TRT |  |
| If external surfaces of the library require cleaning, use a mild detergent solution. Do not use abrasives, solvents, or alcohol based cleaners |  | TRT |  |

# Preventive Maintenance (PM)

## General Information

Wash your hands after applying the lubricants to avoid any possible adverse reaction to one of the lubricants. Refer to the chemical safety data sheet with each lubricant for more information.

If cleaning of the external surfaces of the 3494 is required, it is recommended that you use a mild detergent solution. Do not use abrasives, solvents, or alcohol based cleaners.

## Supplies needed

P/N 0223980 - IBM Lubricant #6

P/N 0435682 – Lubriplate

P/N 1706205 - Swabs (foam tipped)

P/N 34G9329 - Reach Belt

P/N 34G9342 - Pivot Belt

P/N 34G9629 - Y-Axis Drive Belt

P/N 62G1424 - IBM 3495 Track Cable Lubricant (only for leadscrew w/o teflon)

P/N 65F5228 - Krytox Lubricant

Lint-free cloth

## Procedure

Perform the following procedure once a year (or as needed) during a service call. For a high-usage library, perform PM every 500,000 meters traveled on the Y-axis. Select View usage information on the Service Pull-down for the current Y-axis usage.

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| Lubricate the 8 wiper pads 1, 4 and 6 on the X-axis (2 top and 2 bottom) and Y-axis (2 front and 2 back) with IBM Lubricant #6 |  | TRT |  |
| Put a few drops of IBM Lubricant #6 on a cloth and wipe the top and bottom X-rail rods 5 and the front and back Y-rail rods 3 |  | TRT |  |
| Move the grip assembly 7 to the middle of the shafts and apply Krytox lubricant to the shaft 2 on each side of the bearings by using foam-tipped swabs |  | TRT |  |
| Move the grip assembly back and forth on the shafts to load the bearings with lubricant. Wipe off the excessive lubricant on the shafts by using a clean lint-free cloth |  | TRT |  |
| If the library has a teflon-coated (black) leadscrew, DO NOT lubricate the leadscrew. Go to step 7 |  | TRT |  |
| If your library DOES NOT have a teflon-coated leadscrew, lubricate the leadscrew as follows: With the picker assembly at the bottom, wipe the Y-axis leadscrew with a clean lint-free cloth Soak a clean lint-free cloth with IBM 3495 Track Cable Lubricant and apply the lubricant to the exposed length of the leadscrew threads above the leadscrew nut 8. You should see small beads of lubricant on the leadscrew after you have applied it Move the picker assembly up and down the Y-axis to load the leadscrew nut with lubricant |  | TRT |  |
| Apply a thin coat of Lubriplate grease to the front door bracket and pin. The bracket is mounted on the door and the pin is mounted on the frame near the top of the door opening |  | TRT |  |
| If you have a 6 to 8 frame library with the metal band X-axis cable, apply a small amount of Lubriplate grease with a toothpick to the plastic roller shaft of each X-axis long cable support. The long cable supports are located between frames 5 and 6 and between frames 6 and 7 |  | TRT |  |
| Replace the pivot belt, reach belt, and Y-axis drive belt. Refer to “Pivot Belt” on page CARR-31“Reach Belt” on page CARR-42, and “Y-Axis Drive Belt” on page CARR-66 |  | TRT |  |
| Record the date and Y-axis meters traveled for this PM in log book in the clear plastic envelope P/N 1470207 located inside the Model L1x rear door on the top of the display compartment. (See View usage information on the Service Pull-down) |  | TRT |  |

Meters Travelled										Date