IBM Magstar 3494 Tape Library

Maintenance Procedures

Contents

1	Introduction	3

1.1	Overview	3

1.2	Education	3

2	Safety and Inspection	4

2.1	General Information	4

2.2	Preparation	4

2.3	Branch Circuit CB Switched Off Check	5

2.4	Branch Circuit CB Switched On Check	6

2.5	Safety Labels and AC Grounds	7

2.6	Safety Labels and Grounds for the Model L1x	7

2.7	Safety Labels and Grounds for the Model D1x	8

2.8	Safety Labels and Grounds for the Model S10	8

2.9	Safety Engineering Changes	9

2.10	Safety Checks	9

2.11	Completion Report and Signature	10

2.11.1	Safety Hazards	10

3	Library Information Tables	11

3.1	General Information	11

3.2	ARTIC Port Assignments – Figure 272	12

3.3	Teach Configuration – Figure 284	13

3.4	General Library Information – Figure 285	15

3.5	Device Attachment Configuration	17

3.6	Remote Support Information – Figure 286	18

3.7	LAN Information – Figure 287	19

4	Library Verification Checklist	20

4.1	General Information	20

5	Preventive Maintenance (PM)	22

5.1	General Information	22

5.2	Supplies needed	22

5.3	Procedure	22

5.4	Operational Logs	24

5.4.1	Error Logs	24

6	Appendix A – ECAs	25

6.1	Engineering Change Announcements (Sept-2004)	25

7	Appendix B – SMs	28

7.1	Safety Service Memorandums (Sept-2004)	28

# Introduction

## Overview

The procedures in this document ensure that a 3494 not under a TRT maintenance agreement has the necessary prerequisites installed and available to ensure a transparent transition and an uninterrupted maintenance service during the period of the TRT maintenance agreement.

## Education

All service personnel must be trained on the general maintenance agreement qualification, tailored maintenance agreement qualification, and changed machine safety inspection procedures as part of becoming a TRT Technical Service Representative (TSR). In addition, service personnel must also be trained on the 3494 prior to servicing the equipment.

# Safety and Inspection

## General Information

The safety checklist procedures in this topic ensure that a 3494 not under a TRT maintenance agreement has the necessary safety items installed and that no changes made it unsafe. Each 3494, as designed and assembled, has safety items installed to protect operators and service personnel from injury. These checklist procedures verify only these items.

The safety checklist procedures must be performed before the normal inspection for a maintenance agreement. The 3494 must be considered unsafe until the presence and condition of all checklist items are verified. If any unsafe conditions are present, you must decide how serious the hazard is and whether you can continue without first correcting the problem.

When performing the safety checklist procedures, consider the following conditions and the potential safety hazards they present:

- Electrical, especially primary power. For example, an electrically charged frame can cause serious or lethal electrical shock.

- Explosive. For example, damaged or expanding capacitors can cause serious injury.

- Mechanical hazards, such as missing safety covers, can cause injury to service personnel.

## Preparation

The following reference items are useful during the inspection:

- The LOC section of the 3494 Maintenance Information manual

- Copies of safety service memorandums (SMs) (see Appendix B) and engineering change announcements (ECAs) (see Appendix A) for this machine type

- Parts catalog

- 3494 history

- Electrical Safety for TRT Technical Service Representatives

## Branch Circuit CB Switched Off Check

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| Locate and switch off the circuit breaker (CB) for the 3494 branch circuit that supplies voltage to each receptacle |  | TRT / Customer |  |
| Perform one of the following for each receptacle: Note: There is a line cord for each control unit frame and drive unit frame in the library. If this is a metal clad connector, perform the “Safe-to-Handle Check” and the Disconnect Precautions” procedures in Electrical Safety for TRT Technical Service Representatives. (These procedures are described under “Miscellaneous Safety Tips.”) If the power cord has an insulated plug, grip the plug without touching any metal parts, and remove the plug from the customer power receptacle |  | TRT / Customer |  |
| Perform the “Power Receptacle Safety Check” in Electrical Safety for TRT Technical Service Representatives |  | TRT |  |
| DANGER Hazardous voltages are present. Do not touch the internal parts (pins and sockets) of the outlet. Measure the phase-to-ground voltage at each receptacle If a neutral is present, measure the phase-to-neutral voltage, phase-to-ground voltage, and the neutral-to-ground voltage If all voltage values are not less than 1.0 V ac, have an electrician check the circuit |  | TRT |  |

## Branch Circuit CB Switched On Check

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| Switch on the CB that supplies voltage to each receptacle for the library |  | TRT / Customer |  |
| DANGER Hazardous voltages are present. Do not touch the internal parts (pins and sockets) of the outlet. Measure the phase-to-ground voltage at each receptacle If a neutral is present, measure the phase-to-neutral voltage, phase-to-ground voltage, and the neutral-to-ground voltage Record the voltages for future reference in the checklist shown in the following table |  | TRT |  |
| Switch off the branch circuit CB before connecting the machine power cord into the outlet |  | TRT / Customer |  |

| Voltage Checklist |
| --- |
| Date | Description of circuits checked | Voltage Values | Comments | TSR |

## Safety Labels and AC Grounds

Understand the meaning of the safety labels before beginning any repair of a component with a label.

Check that the labels are located where shown in following figures. Make any necessary corrections. See IBM 3494 Tape Library Dataserver Parts Catalog for part numbers of labels in the various languages.

## Safety Labels and Grounds for the Model L1x

## Safety Labels and Grounds for the Model D1x

Use the previous figure keys 6 through 8 and 10 through 12 for the locations of the safety labels and grounds in the drive unit frame.

## Safety Labels and Grounds for the Model S10

The storage unit frame does not contain any safety labels or grounds.

## Safety Engineering Changes

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| All safety engineering changes (ECs) have been installed correctly |  | TRT |  |
| The location or list of engineering change announcements (ECAs) is accessible |  | TRT |  |

## Safety Checks

The 3494 must be powered off with the power cable disconnected.

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| All hinges and latches are in acceptable operating condition and are not broken or corroded |  | TRT |  |
| All door interlocks and safety switches are operating and are not bypassed with jumpers or taped closed |  | TRT |  |
| All ac line cords are not frayed or damaged |  | TRT |  |
| All ac line cords have the correct part number Note: See IBM 3494 Tape Library Dataserver Parts Catalog for the correct part number for the power cables. See also IBM 3494 Tape Library Dataserver Introduction and Planning Guide |  | TRT |  |
| All ground jumpers (normally green and yellow) are tightly attached. Check that all covers, housings, and metal box sides have proper ground continuity (less than 0.1 ohm) |  | TRT |  |
| All ground connections are tightly attached |  | TRT |  |
| Check from the library manager chassis to the control unit frame for proper ground continuity (less than 0.1 ohm) |  | TRT |  |
| The resistance from the library manager line cord ground pin to the frame and to the power supply covers must not be more than 0.1 ohm. For the ground connection locations, see Figure 211 on page INSP-7 |  | TRT |  |
| All safety covers (operator and service areas) are in place including those protecting mechanical devices and hot surfaces. No sharp corners or edges should be unprotected. All access covers must be in place |  | TRT |  |
| The customer’s circuit breakers and circuit panels for the 3494 frames are identified as 3494 branch circuits |  | TRT |  |
| All ac output safety covers are installed |  | TRT |  |
| No obvious non-IBM changes have been made |  | TRT |  |
| No metal filings, dirt, contaminants, water, or other fluids are present |  | TRT |  |
| There are no marks from earlier smoke or burning |  | TRT |  |
| The ac power supplies are attached tightly in place |  | TRT |  |
| The ac line cords have no frayed or damaged wiring at the PCCs |  | TRT |  |
| The resistance from the line cord ground pins and housings to all frames and to all power assembly grounds are: Line cord ground pin to frame ground resistance must not be more than 0.1 ohm Line cord housing to frame ground resistance must not be more than 0.1 ohm |  | TRT |  |
| All power wiring does not have frayed or damaged wires |  | TRT |  |
| The dc power supplies are attached tightly in place |  | TRT |  |
| All circuit breakers are the correct size. See IBM 3494 Tape Library Dataserver Parts Catalog |  | TRT |  |
| All cables, connections, and plugs do not have frayed or damaged wiring |  | TRT |  |
| All latches or clamps are in acceptable condition |  | TRT |  |

## Completion Report and Signature

- Safety inspection for machine type 3494

- General safety inspection

- Maintenance agreement qualification

After the inspection, sign and date the checklist and store it with the maintenance job paperwork.

Name										Date

### Safety Hazards

List all safety hazards, if there are none, write none.

# Library Information Tables

## General Information

The following library information tables are provided to record vital library information for new maintenance agreements or new TSRs that may not be familiar with this account.

Complete the following general information tables for this library and place the following sheets (or a copy) in the clear plastic envelope P/N 1470207 located inside the Model L1x rear door on the top of the display compartment along with any appropriate local information:

- ARTIC Port Assignments. See Figure 272 or INST-98

- Teach Configuration. See Figure 284 or INST-124

- General Library Information. See Figure 285 or INST-135

- Device Attachment Configuration. DIAG-6

- Remote Support Information. See Figure 286 or INST-137

- LAN Information. See Figure 287 or INST-139

## ARTIC Port Assignments – Figure 272

## Teach Configuration – Figure 284

## General Library Information – Figure 285

| Figure 285. General Library Information |
| --- |
| Description | Library S/N ______________ |
| LM Hardware Configuration: | MT____________ Model_____________ Processor___________________ (chkfins) Memory____________________ (qphymem) Disk_______________________ (chkdsk) Disk_______________________ (chkdsk) Disk_______________________ (chkdsk) Disk_______________________ (chkdsk) |
| Optional LM Features: | FC 5050, Dual Active Accessor --------- Yes____ No____ FC 5214, 2nd Disk Drive for LM ----- Yes____ No____ FC 5219, Token Ring Adapter ---------- Yes____ No____ (lancheck) FC 5220, Ethernet Adapter -------------- Yes____ No____ (lancheck) FC 5226, LM Remote Console -------- Yes____ No____ FC 5229, Expansion Attachment Card - Yes____ No____ FC _____ FC _____ FC _____ |
| 3494 Manuals/Tools: 3494 Operator's Guide 3494 LIC 3494 MI 3494 VTS MI 3494 Tool Kits 3490 _____ MI 3490 _____ MI 3590 _____ MI 3590 _____ MI | Location: ________________________________________________________ Location: ________________________________________________________ Location: ________________________________________________________ Location: ________________________________________________________ Location: ________________________________________________________ Location: ________________________________________________________ Location: ________________________________________________________ Location: ________________________________________________________ Location: ________________________________________________________ |
| ECA’s Installed: | ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: ECA ______ Date __________ Comments: |
| LM code level: | OS/2_________ (syslevel) LM___________ (chkfins) |
| Drive code level: | Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: Model _______-_____ Code___________ Location____________ Comments: |

## Device Attachment Configuration

Select Device Attachment Configuration on the Teach Pull-down for the ARTIC port assignments for the library. Detail the configuration in the space provided below.

## Remote Support Information – Figure 286

## LAN Information – Figure 287

# Library Verification Checklist

## General Information

Use the following checklist to verify that the library is installed correctly and ready for TRT maintenance.

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| All leveling pads are snug against the floor |  | TRT |  |
| The X-rail in each frame is aligned vertically and horizontally |  | TRT |  |
| The X-rail is straight and level within 3 mm over 4 frames |  | TRT |  |
| The X-rail upper and lower bearing rods on each frame are touching the previous rods |  | TRT |  |
| The rear aisle frame member of the end frames is plumb within 4 mm |  | TRT |  |
| Four frame attach brackets are installed between each expansion frame |  | TRT |  |
| All frame spacer bolts are installed between each expansion frame |  | TRT |  |
| The upper rail in each frame is locked and aligned from side-to-side |  | TRT |  |
| The center upper rail rollers do not touch the rail in any frame |  | TRT |  |
| The accessor can reach the last column of cartridges on each side without touching the X-axis bumper |  | TRT |  |
| The accessor moves freely and quietly along the length of the library |  | TRT |  |
| The lower and middle storage arrays are sitting down tight against the support bracket or drive sleeve |  | TRT |  |
| The upper storage arrays are sitting down tight against the lower storage array (or bracket) |  | TRT |  |
| There is no gap between the upper and lower storage array side brackets on either side |  | TRT |  |
| The storage array cells in each frame are not damaged or nicked and all empty cell labels are present |  | TRT |  |
| If the library has a dual gripper, storage inserts are installed and fully seated in the upper and lower two rows of each frame |  | TRT |  |
| All screw heads behind the storage array fiducials are covered with a black plastic sleeve |  | TRT |  |
| The door pin (if adjustable) touches the door support bracket on each frame when the door is closed. All doors should open and close freely |  | TRT |  |
| Each door latch is adjusted so the door is tight against the frame when the door is locked |  | TRT |  |
| If your library has an X cable with a metal band, ensure the X-axis cable tracks correctly without touching the drive covers, cable trough edge, or X-rail |  | TRT |  |
| Each 3490 CxA deck is pulled forward in the sleeve and the retaining screws are tight |  | TRT |  |
| Each 3490 CxA drive sleeve has a retaining screw installed in the rack at the rear of the sleeve |  | TRT |  |
| Each 3490 F1A drive has both slide retaining screws installed |  | TRT |  |
| Each 3590 drive has a slide retaining screw installed at the rear of the drive |  | TRT |  |
| Verify that the distance between the front of the picker reach platform and the cartridge label surface is 35 mm or less on each frame at the drive unload point and at the storage rack |  | TRT |  |
| All screw heads behind the 3490 drive fiducials are black |  | TRT |  |
| All fiducials were located successfully during the Teach operation |  | TRT |  |
| The library manager microcode and all microcode in the 3490 and/or 3590 tape subsystems is at the latest released level |  | TRT |  |
| The Verify Installation tests ran successfully on each new frame and drive |  | TRT |  |
| If the customer does not need the library immediately, run 10 cycles of the Frames Alignment test with all new frames selected and 5 cycles of the Drive Get/Put test with all new drives selected. Check the logs for errors after each test completes |  | TRT |  |
| Check the customer has sufficient cleaning cartridges that were shipped with the library |  | TRT |  |
| Ensure that the Licensed Internal Code (LIC) backup diskettes and library manager diagnostic diskettes are stored in the supplied binder SA37-0300 |  | TRT |  |
| Ensure the front and rear door keys, 3494 tools and books are close to the library for service activity |  | TRT |  |
| If external surfaces of the library require cleaning, use a mild detergent solution. Do not use abrasives, solvents, or alcohol based cleaners |  | TRT |  |

# Preventive Maintenance (PM)

## General Information

Wash your hands after applying the lubricants to avoid any possible adverse reaction to one of the lubricants. Refer to the chemical safety data sheet with each lubricant for more information.

If cleaning of the external surfaces of the 3494 is required, it is recommended that you use a mild detergent solution. Do not use abrasives, solvents, or alcohol based cleaners.

## Supplies needed

P/N 0223980 - IBM Lubricant #6

P/N 0435682 – Lubriplate

P/N 1706205 - Swabs (foam tipped)

P/N 34G9329 - Reach Belt

P/N 34G9342 - Pivot Belt

P/N 34G9629 - Y-Axis Drive Belt

P/N 62G1424 - IBM 3495 Track Cable Lubricant (only for leadscrew w/o teflon)

P/N 65F5228 - Krytox Lubricant

Lint-free cloth

## Procedure

Perform the following procedure once a year (or as needed) during a service call. For a high-usage library, perform PM every 500,000 meters traveled on the Y-axis. Select View usage information on the Service Pull-down for the current Y-axis usage.

| Task | Date | Owner | ( / ( |
| --- | --- | --- | --- |
| Lubricate the 8 wiper pads 1, 4 and 6 on the X-axis (2 top and 2 bottom) and Y-axis (2 front and 2 back) with IBM Lubricant #6 |  | TRT |  |
| Put a few drops of IBM Lubricant #6 on a cloth and wipe the top and bottom X-rail rods 5 and the front and back Y-rail rods 3 |  | TRT |  |
| Move the grip assembly 7 to the middle of the shafts and apply Krytox lubricant to the shaft 2 on each side of the bearings by using foam-tipped swabs |  | TRT |  |
| Move the grip assembly back and forth on the shafts to load the bearings with lubricant. Wipe off the excessive lubricant on the shafts by using a clean lint-free cloth |  | TRT |  |
| If the library has a teflon-coated (black) leadscrew, DO NOT lubricate the leadscrew. Go to step 7 |  | TRT |  |
| If your library DOES NOT have a teflon-coated leadscrew, lubricate the leadscrew as follows: With the picker assembly at the bottom, wipe the Y-axis leadscrew with a clean lint-free cloth Soak a clean lint-free cloth with IBM 3495 Track Cable Lubricant and apply the lubricant to the exposed length of the leadscrew threads above the leadscrew nut 8. You should see small beads of lubricant on the leadscrew after you have applied it Move the picker assembly up and down the Y-axis to load the leadscrew nut with lubricant |  | TRT |  |
| Apply a thin coat of Lubriplate grease to the front door bracket and pin. The bracket is mounted on the door and the pin is mounted on the frame near the top of the door opening |  | TRT |  |
| If you have a 6 to 8 frame library with the metal band X-axis cable, apply a small amount of Lubriplate grease with a toothpick to the plastic roller shaft of each X-axis long cable support. The long cable supports are located between frames 5 and 6 and between frames 6 and 7 |  | TRT |  |
| Replace the pivot belt, reach belt, and Y-axis drive belt. Refer to “Pivot Belt” on page CARR-31“Reach Belt” on page CARR-42, and “Y-Axis Drive Belt” on page CARR-66 |  | TRT |  |
| Record the date and Y-axis meters traveled for this PM in log book in the clear plastic envelope P/N 1470207 located inside the Model L1x rear door on the top of the display compartment. (See View usage information on the Service Pull-down) |  |  |  |

Meters Travelled										Date

## Operational Logs

The logs of the 3494 capture error and transaction data. This data is used for error recovery, for debugging software, and for aiding in the development and support of the product. Of these logs, the service representative uses only the error log and, to some extent, the transaction log. Logs are rotated by using a push-down method. The most current log is at the top of the log group of the Service menu. When the log is full, it is pushed down, and the oldest log in the stack is overwritten and rotated to the top of the stack to become the new current log. View the transaction and error logs by selecting View Logs from the Utilities menu of the library manager.

### Error Logs

To display an error log, select Analyze Error Log from the Service pull-down. Select this option to analyze the library manager error log entries. This selection identifies the record group for an event, separates the information records, and displays the error code for the most important error record. The last five error records are displayed. Please record all recent errors are there details.

| Error Logs |
| --- |
| Date / Time | Component | ECOD – ERPC – LMM | Optional Message | TSR |
| 04.123 14:04 | EH21 | 8604 – 75E0 – 00110 | ERP CHECK1 is being processed. | CS |

Refer to REPORTS-10 for further information in analyzing the error log entries.

# Appendix A – ECAs

## Engineering Change Announcements (Sept-2004)

ECA   EC NUMBER   B/M #     DATE   TIME   DESCRIPTION

___   _________   _______   MM-YY  ____   ____________

001   C88489  *** OBSOLETE  06-94   1.0   LM50A.09

002   C88494  *** OBSOLETE  06-94   0.5   LM BACKUP DISKETTES

003   C88711      05H1968   07-94   1.0   MIC CARD FUSES

004   C88708  *** OBSOLETE  07-94   0.2   MI UPDATE/PARTS CATALO

005   C88491  *** OBSOLETE  09-94   1.0   LM50C.00

006   C88722  *** OBSOLETE  09-94   0.2   AIX DRIVER

007   C88746  *** OBSOLETE  01-95   0.2   UPDATE MI TO -02 LVL

008   C88492A *** OBSOLETE  04-95   4.0   UPDATE OS2 2.1-LM50D03

009   C88496  *** OBSOLETE  04-95   1.0   OS2 2.11 49 DAY FIX

010   C88693  *** OBSOLETE  04-95   0.2   ***obsoleted by eca015

011   C88694  *** OBSOLETE  05-95   0.5   UPDATE AS400 LAN DDRV

012   C34939  *** OBSOLETE  09-95   0.2   ***obsoleted by eca026

013   c34952      05h7608   09-95   0.5   line cord safety check

014   c34962      05h7622   12-95   3.0   leadscrew replacement

015   c34966  *** OBSOLETE  11-95   0.2   Risc Lan Dev Drvr

016   c88758  *** OBSOLETE  12-95   ***   Upgrade to LM50f03

017   d19118      05h7700   12-95   0.5   3590 code update >3494

018   c34974      05h7725   04-96   2.0   clips/insp barcode/gri

019   c88739a     05h7726   04-96   2.0   replace barcode reader

020   C88675A     05H7706   04-96   1.5   replace GRI gripper cd

021   c88592a     05h4800   03-96   0.3   Jap/German User's gds

022   c88846      05h7700   06-96   0.5   Update 3590 code 3f2

023   c34994      05h3944   06-96   0.2   Device Driver lan risc

024   c88760  *** OBSOLETE  06-96   5.0   mcode lm511.05

025   c34997      05h7757   07-96   1.3   barcode module eeprom

026   c35056      05h8189   02-97   0.2   replace mi >> 5th edit

027   c35091  *** OBSOLETE  07-97   4.2   hw hardening fixes

028   c70576      05h9290   08-97   0.5   30 CTG IO SENSOR FIX

029  OBSOLETE *** OBSOLETE                OBSOLETE

030   d19291      05h7249   10-97   0.6   insp cable trough spcr

031   c34970      05h7193   10-97   2.5   rmt lm code/ii's

032   c88764      05h7135   10-97   1.5   lm code 51405/db2 csd

033   C35078A     05h4047   11-97   0.5   B16 MI UPDATE

034   C70608B     -------   -----   -.-   dummy ec xcable 5-8frm

035   C70671      05H8637   03-98   1.3   inbay magnet repl ha1

036   F23117  *** OBSOLETE  06-98   1.6   insp repl 7133 fan+pwr

037   F23153      05H8810   07-98   2.6   amex x+pivot flex cabl

038   F23117A *** OBSOLETE  08-98   1.6   fan pwr sup repl7133

039   F23185  *** OBSOLETE  08-98   2.5   lm 51802 warp 4 fix ha

040   F23216      08L6129   08-98   0.7   ha1 door inlk cbl fr89

041   ECA041 obsolete ******************  obsoleted by eca042

042   F23190C     05H8871   10-98   2.0   pga3 vts 518 os2 mims

043   F23158      05H8800   11-98   2.3   ha1 repl mic3 w mic4

044   F23227A     08L5910   11-98   3.0   ha1 enable on b18

045   F23299      08L6052   01-99   3.0   Mem upgrade ha1 lm prf

046   D19270B     08L6020   11-98   2.5   Replace rear and side

black covers w/white

047   D19270B     08L6020   11-98   2.5   Replace rear black

covers w/white

048   F23223A     35L0573   10-99 1.5/12.5 LM_CU_DRV Code plus

049   F24227A     09L5297   08-99 2.0/3.0 Relace Pivot Cam Asm

050   F24350      35L0162   10-99   0.5   Power cord inspection

051   F24350A     35L0207   10-99   1.5   Power cord replace US

35L0208   10-99   1.5   Power cord replace WT

052  CANCELLED

053  CANCELLED

054  CANCELLED

055   F23223C     35L0819   01-00   2.8   LM/B16/Axx/B1A/E1A

35L0820           to        code

09L5135           8.8

09L5136

09L5137

056   D19426      35L1630   03-00   1.5   3590 sars code library

A_429 B_7B2 C_747

057   H27341      19P0546   07-00   1.5   Disable SCSI term on

A60 D14 Adjacent Frame

058   H27357B     19P1055   10-00   0.3   Replace CE null modem

cable

059   H27392      19P0716   10-00   1.5   Replace 8M SCSI cable

adjacent frame 6M

060   H27739      19P2753   03-01   5.7   Install VTS code

2.22.19.1 B18 AX0

061   H27497      19P1385   05-01   5.7   VTS  2.17.22.3

Note: If VTS code is currently below      LM   523.01 + EF .18

2.17.14.X and AIX 4.3.2, this       OS2  Version 3

EC will enable VTS CALLHOME         AIX 4.3.2 + FixPak 6

062   H27497A     19P2109   05-01   5.7   Same as ECA061

(w code 2.17.14.5 up to 2.21.12.1)

063   H27493A     19P2943   06-01   2.0   7588 > 400Mhz

> 256 meg mem

064   H27689B *** OBSOLETE  10-01   2.0   Install HW

memory,Hard drv,NIC

065   H27924      19P3939   10-01   4.5   B18 2.22.25.2 code

9.5   PtP

066   H28056      19P4724   11-01   0.8   B10 IO drawer rails

missed in mfg

067   H27452C     19P4852   12-01   1.0   Resize D: f: drives

-3.5   optimize dump +logging

068   H80030      19P5442   03-02   2.0   Replaces ECA064

Install hw

memory,Hard Drv,nic

070   H80001A     18P6421   08-02   0.1   Update VTS MI and in

some cases ESCON card

071   CANCELED

072   CANCELED

073   H80001D     Multiple  12-02   8.5   VTS to 2.23.36.0

or higher

074   H80001D     Multiple  12-02   8.5   VTS PtP to 2.23.36.0

or higher

075   H80070      18P7184   05-03   1.5   A50 Code 1.10.10.3

A60 Code 1.15.14.6

076   H80486      18P7635   04-03   6.0   VTS replaces early

2.26.x levels with

2.26.26.0

077   H80450      18P7678   04-03   3.0   LM527.15 to solve

49.7 day hang

079   H80118B     24R0290   02-04   0.5   3590 E1A/H1A Code

Time is per drive

080   H80743A     Multiple  04-04   1.5   LM/CU/Drive code

8.0   for 3592 support.

***   See IIs for actual

times.

081   H80911      24R0912   04-04   0.5   D22 service panel

mounting hardware

replacement/move.

500   H80001      None      05-02   N/A   Used for reporting

install of VTS code

2.23.31.88 shipped

from PFE

501   H80486      None      03-03   N/A   Used for reporting

install of VTS code

2.26.26.0 shipped

from PFE

502   H80450      None      03-03   N/A   Used for reporting

install of LM527.15

code shipped from PFE

503   None        None      10-03   N/A   Used for reporting

inst of AIX Fixpack 11

for VTS 2.26 or 2.27

504   None        None      11-03   N/A   Used for reporting

inst of R7 for memory

leak problem corrected

in fixpack 11.

733   None        None      08-00   N/A   Used for PFE Hardware

action plan

910   Pseudo      None      10-03   N/A   Used for PFE directed

code load to fix mach

problem.

Includes leveling all

machines in one acct.

920   Pseudo      None      10-03   N/A   Used when code load is

required/recommended

during new machine

install.

930   Pseudo      None      10-03   N/A   Used when 3494 code

update is required

for add/alteration

of another mach type

in library.

Example:3590/3592

upgrade which requires

3494 LM code update.

940   Pseudo      None      10-03   N/A   Used when code has

to be updated for

FRU usage.

Example:PFE_Execs or

fixlevel required for

SSA Pdisk FRU.

# Appendix B – SMs

## Safety Service Memorandums (Sept-2004)

Abstract:  SAFETY 3494 L1X AND D1X LINE CORD CONNECTOR INSPECTION

***** SAFETY ****

TEXT: A potential line cord safety exposure exists on

frames with single-phase line cords.

Subject: Potential Safety Exposure on 3494 Machines

*************************************************

* This is a "compliance to safety standards"    *

* alert which requires mandatory action.  This  *

* action needs to be completed within 90 days.  *

*************************************************

Machine Types:   3494

Models Affected: L10, L12, L14

Problem:

-------

A defect may exist with the ground pin in the plug of the input power cord for the models listed above.  This power plug can be recognized by the Russellstoll 3750DP designation on the plug end. The Russellstoll 3750DP plug has three pins.  On a normal (non-defective) plug, the ground pin has a larger diameter than the two phase pins. On a defective plug all three pins have the same "small" diameter.

With all of the pins being the same size, the "keying" mechanism that would normally ensure correct "phase-to-phase" and "ground-to-ground" connections is defeated.

Defect Impact:

1) If a defective plug is connected in the CORRECT

orientation, the safety ground may not be making a

proper connection.

2) If a defective plug is connected in the WRONG

orientation, the machine will NOT power-on.

However, it is possible for the machine frame to be

at a HAZARDOUS VOLTAGE LEVEL.

*************************************************************

*   The following inspection procedure MUST be performed:   *

*      * Prior to powering-on ANY newly-installed or        *

*        relocated machines.                                *

*      * For ALL machines already installed.                *

*************************************************************

Time and materials associated with this inspection and the correction of any defect can be accounted for by using ECA029.